Instructions for regular maintenance of
the lighting system
Regular maintenance of luminaires must be carried out at regular intervals with respect to the product type and according to use in different types of environments such as dusty, very dusty, with the presence of oil steams and more.
Regular maintenance according to the instructions in this document should be carried out for all luminaires supplied by Alphalighting CZ Ltd.
List of the used abbreviations:
PC - Polycarbonate
PMMA - Polymethylmethacrylate
Instructions for a range of regular maintenance of various types of luminaires are as follows:
[bookmark: 3znysh7]* Industrial luminaires with a fiberglass body and
diffuser made of PC and PMMA material

1. Subject of regular maintenance
The subject of regular maintenance is cleaning the outer surface of the upper diffuser and fiberglass cover of the luminaire. Before starting maintenance, equipment must be turned off, if the luminaires are hot from previous use, they must be let to cool down.
[bookmark: _Hlk491811056]The diffuser can be wiped with a damp cloth (using nonionic detergents and water), remove any dirt or smear, let it dry. In case of pollution by lipophilic contaminants such as oils, a cloth to which ISOPROPYL ALCOHOL is applied, can be used to gently rub these dirt deposits.
Dirt on the top of fiberglass luminaire cover should be wiped away or vacuumed as a prevention of pollution of the manufacturing equipment and materials in the production area. In case of the pollution by lipophilic contaminants such as oils, we follow the same instructions as for the pollution of the diffuser.
During maintenance and cleaning of luminaires any etchants or solvents of gasoline, alcohol, toluene, thinner type and the like must not be used.
Proper lighting system efficiency is dependent on the purity and surface reflectivity of the room. To ensure the necessary reflection of the walls painting white 1x per 3 years is recommended.
Caution: Regular maintenance can only be performed by a skilled qualified electrician.

2. Interval of regular maintenance
The user is obliged to carry out regular cleaning at least 1x year.
In the event of luminaire failure, this is solved by replacing the light source, which can only be done by the manufacturer, see. General warranty terms Alphalighting CZ.
Caution: Regular records must be kept on the regular maintenance of luminaires, for example in the log book of the lighting system!!!
❖ Industrial lights with metallic aluminum body and diffuser made of PC, PMMA and glass material
1. Subject of regular maintenance
The subject of regular maintenance is exterior surface cleaning of the diffuser from PC, PMMA or glass, the cooling ribbing on the top of the aluminum bodies or luminaires, metal body of the luminaire. Before starting maintenance, the equipment must be turned off, if the lights are hot from previous use, they must be let to cool down.
The diffuser can be wiped with a damp cloth (using nonionic detergents and water), remove any dirt or smear, let it dry. In case of pollution by lipophilic contaminants such as oils, a cloth to which ISOPROPYL ALCOHOL is applied, can be used to gently rub these dirt deposits.
Dirt between the ribs on the top of the luminaire should be vacuumed. If the luminaire is used in very dusty environments and between the ribs there is a layer of dust deposits, it is necessary to blow it off with compressed air, preferably in the open area. A cloth should be used to remove the rest of the dirt, which would impede the effective functioning of the luminaire cooling system. In case of pollution by lipophilic contaminants such as oils, a cloth to which ISOPROPYL ALCOHOL is applied, can be used to gently rub these dirt deposits. In the case of the clogging of the luminaire´s cooling part malfunction of the internal electronics cooling occurs and this reduces durability, performance, or causes failure of the luminaire.
[bookmark: _Hlk491813603]During maintenance and cleaning of luminaires any etchants or solvents of gasoline, alcohol, toluene, thinner type and the like must not be used.
Proper lighting system efficiency is dependent on the purity and surface reflectivity of the room. To ensure the necessary reflection of the walls painting white 1x per 3 years is recommended.

Caution: Regular maintenance can only be performed by a skilled qualified electrician.
2. Interval of regular maintenance
The user is obliged to carry out regular cleaning at least 1x year. In the case of the use of luminaires in a very dusty environment, it is necessary to inspect and clean the cooling system of the luminaire 1x in 6 months.
In the event of non-regular maintenance, the warranty of the luminaire that has a defect, may not be recognized.
· the event of luminaire failure, this is solved by replacement of the light source, which can only be done by the manufacturer, see General warranty terms Alphalighting CZ.
Caution: Regular records must be kept on the regular maintenance of luminaires, for example in the log book of the lighting system!!!
[bookmark: lnxbz9]* Indoor (OFFICE) luminaires with diffuser from
PC, PMMA and glass material
1. Subject of regular maintenance
The object of regular maintenance is cleaning of the outer surface of the diffuser and luminaires with cover lower than IP 5X and inner parts of the diffuser. Before starting maintenance, equipment must be turned off if the lights are hot from previous use, they must be let to cool down.
[bookmark: _Hlk491814524]The diffuser can be wiped with a damp cloth (using nonionic detergents and water), remove any dirt or smear, let it dry. In case of pollution by lipophilic contaminants such as oils, a cloth to which ISOPROPYL ALCOHOL is applied, can be used to gently rub these dirt deposits.
During maintenance and cleaning of luminaires any etchants or solvents of gasoline, alcohol, toluene, thinner type and the like must not be used.
Proper lighting system efficiency is dependent on the purity and surface reflectivity of the room. To ensure the necessary reflection of the walls painting white 1x per 3 years is recommended.

Caution: Regular maintenance can only be performed only a skilled qualified electrician.
2. Interval of regular maintenance
The user is obliged to carry out regular cleaning at least 1x in two years.
In the event of lamp failure, this is solved by replacement of the light source, which can only be done by manufacturer, see General warranty terms Alphalighting CZ.
Caution: Regular records must be kept on the regular maintenance of luminaires, for example in the log book of the lighting system!!!

❖ Outdoor (STREET) luminaires
1. The subject of regular maintenance
The subject of regular maintenance is cleaning of only the outer surface of the diffuser. Before starting maintenance, the equipment must be turned off if the lights are hot from previous use, they must be let to cool down.
The diffuser can be wiped with a damp cloth (using nonionic detergents and water), remove any dirt or smear, let it dry. In case of pollution by lipophilic contaminants such as oils, a cloth to which ISOPROPYL ALCOHOL is applied, can be used to gently rub these dirt deposits.
During maintenance and cleaning of luminaires any etchants or solvents of gasoline, alcohol, toluene, thinner type and the like must not be used.
Proper lighting system efficiency is dependent on the purity and surface reflectivity of the room. To ensure the necessary reflection of the walls painting white 1x per 3 years is recommended.

Caution: Regular maintenance can only be performed by a skilled qualified electrician.
2. Interval of regular maintenance
The user is obliged to carry out regular cleaning at least 1x in two years.
In the event of lamp failure, this is solved by replacement of the light source, which can only be done by the manufacturer, see General warranty terms Alphalighting CZ.
[bookmark: _GoBack]Caution: Regular records must be kept on the regular maintenance of luminaires, for example in the log book of the lighting system!!!

